Suggested Specification for Wafer Silent Check Valve

Check valve shall be of the silent wafer type and the same size as the entering pipe. Valves

shall be the compact wafer style and have a pressure and temperature rating equal to

or greater than the pipeline in which they are installed. Compact wafer-silent style check

valves thru 12 inches shall be rated for 250PSI WOG for installation between ANSI Class

125 or Class 250 flanges, have a Ductile Iron body (ASTM A-536 65-45-12), ASTM Type 316 Stainless Steel helical or conical spring, ASTM 304 Stainless steel valve seat with integral EPDM seat seal,  ASTM Type 304 dual guided disc (top and bottom), 304 Stainless Steel guide bushing and type 304 Stainless Steel guide pins. Valves are to operate silently in either vertical or horizontal positions, flow up or down. Compact wafer-silent check valve shall be Pratt Series 720A as manufactured by the Henry Pratt Company.